SEWS 10.1.1 (1 of 3)	Sheet 1 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) |  |
| --- | --- |
| Piping System ID No.: | Equipment Class: Piping |
| Performance Category: |  |
| System Description and Fluid Boundaries: |  |
| Piping System Function and Contents |  |
| Operability Pressure Boudary Position Retention |  |
| Piping Layout and Structural Boundaries Piping System Location and Reference Drawings |  |
| Piping Materials and Sizes |  |
| Weights |  |
| Concurrent Pressure and Temperature |  |
| Input Response Spectra and SAM-Reference |  |
| Final Preliminary |  |
| Applicability Ductile material D/t<50 -20°F ≤ T ≤ 250°F Reference Spectra |  |

SEWS 10.1.1 (2 of 3)	Sheet 2 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) (Cont.) |  |  |  |
| --- | --- | --- | --- |
| Piping System ID No.: |  | Equipment Class: Piping |  |
| Screening Criterion (Section 10.1.1) | Screening Criterion Met |  | Notes |
| Construction: Piping, components and supports shall be undamaged and of good construction. |  |  |  |
| Internal Degradation: Piping and components shall be free of signigicant internal degradation. |  |  |  |
| External Corrosion: Piping, components and supports shall be free of significant external corrosion. |  |  |  |
| Vertical Span: Piping shall be well supported vertically. |  |  |  |
| Lateral Span: Piping shall be sufficiently restrained in the lateral direction. |  |  |  |
| Anchor Motion: Piping shall have sufficient flexibility to accommodate the seismic motions of structures, equipment and headers to which it is attached. |  |  |  |
| Mechanical Joints: Piping shall not contain mechanical joints which rely solely on friction. |  |  |  |
| Flanged Joints: Flanged joints shall withstand the expected seismic moments without leakage. |  |  |  |
| Equipment Nozzle Loads: Equipment shall not be subjected to large seismic loads from the piping systems. |  |  |  |
| Eccentric Weights: Eccentric Weights in piping systems shall be evaluated. |  |  |  |
| Flexible Joints: Flexible joints shall be properly restrained to keep relative end movements within vendor limits. |  |  |  |
| Evaluation of Pipe Supports: Pipe supports shall be capable of withstanding seismic loads without failure. |  |  |  |
| Interaction with Other Components: The piping being reviewed shall not be a source of interactions by displacement or swing impact on adjacent components. |  |  |  |
| No other concerns |  |  |  |

SEWS 10.1.1 (3 of 3)	Sheet 3 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) (Cont.) |  |
| --- | --- |
| Piping System ID No.: | Equipment Class: Piping |
| Comments |  |
| Screening Walkdown(s): Date Time Team Members |  |
| Recommend Resolution |  |
| q Maintenance action: q Further evaluation: q Retrofit design: q Other: q No further action required. Equipment is seismically adequate. |  |
| All aspects of the equipment's seismic adequacy have been addressed. Evaluation by: Date: (All team members) |  |