SEWS 8.1.3 (1 of 4)	Sheet 1 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) |  |  |
| --- | --- | --- |
| Equipment ID No.: | Equipment Class: Low-Voltage Switchgear |  |
| Equipment description: |  |  |
| Equipment Location: Bldg. | Floor El. | Room, Row/Col. |
| Manufacturer, model, etc.: |  |  |
| Weight of each Cabinet: |  |  |
| Drawing No.: | Performance Category: |  |
| Functionality Requirement |  |  |
| q Contact Lead Relay Reviewer to determine if item contains Essential Relays q For components whose function or structural integrity is required, complete all sections of this form. q For all other components, only anchorage evaluation is required. |  |  |
| Seismic Capacity vs. Demand (Chapter 5) |  |  |
| 1. Seismic Capacity based on: q Reference Spectrum q GERS q Existing documentation 2. Elevation where equipment receives seismic input Seismic Demand Spectrum (SDS) based on: q In-structure response spectrum (IRS) per DOE-STD-1020 q Other in-structure response spectrum (determine appropriate experience data scale factor) q Design basis earthquake (DBE) per DOE-STD-1020 q Other Scale Factor (SF) Experience Data Factor (FED) Does capacity exceed demand? Y N U Reference: |  |  |
| Caveats (Section 8.1.3) |  |  |
| Reference Spectrum (Identify with an asterisk (*) those caveats which are met by intent without meeting the specific wording of the caveat rule and explain the reason for this conclusion in the COMMENTS section below) |  |  |
| 1. Equipment is included in earthquake experience equipment class Y N U N/A 2. 600 V rating or less Y N U N/A 3. Side-to-side restraint of draw-out circuit breakers is provided Y N U N/A 4. Adjacent cabinets which are close enough to impact, or sections of multi-bay cabinets, are bolted together if they contain essential relays Y N U N/A 5. Attached weight (except conduit) less than about 100 lbs per cabinet assembly Y N U N/A 6. Externally attached items rigidly anchored Y N U N/A 7. General configuration similar to ANSI C37.20 standards Y N U N/A |  |  |

SEWS 8.1.3 (2 of 4)	Sheet 2 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) (Cont.) |  |
| --- | --- |
| Equipment ID No.: | Equipment Class: Low-Voltage Switchgear |
| Equipment description: |  |
| Caveats (Cont.) |  |
| 8. Cutouts in lower half of cabinet side sheathing less than 30% of width of side panel wide and less than 60% of width of side panel excluding bus transfer compartment Y N U N/A 9. All doors secured by latch or fastener Y N U N/A 10. Have you looked for and found no other adverse concerns? Y N U N/A Is the intent of all the caveats met for Reference Spectrum? Y N U N/A |  |
| GERS (Identify with an asterisk (*) those caveats which are met by intent without meeting the specific wording of the caveat rule and explain the reason for this conclusion in the COMMENTS section below) |  |
| 1. Equipment is included in generic seismic testing equipment class Y N U N/A 2. Meets all Reference Spectrum caveats Y N U N/A 3. Floor-mounted enclosure Y N U N/A 4. Manufactured by major vendor (ITE/Brown Boveri, Westinghouse, or GE) Y N U N/A 5. Average weight per section less than 1,600 lbs Y N U N/A 6. For 2.5g level GERS, vertical restraint prevents breaker uplift Y N U N/A 7. For 2.5g level GERS, outside corners of end units are reinforced, if needed Y N U N/A 8. Adjacent cabinets which are close enough to impact, or sections of multi-bay cabinets, are bolted together Y N U N/A Is the intent of all the caveats met for GERS? Y N U N/A |  |
| Anchorage (Chapter 6) |  |
| 1. Type of anchorage: q expansion anchor q cast-in-place bolt or headed stud anchor q cast-in-place J-bolt q grouted-in-place bolt q welds to embedded steel on exposed steel q lead cinch anchors q Other q N/A (no further anchorage considerations) 2. Appropriate characteristics for anchorage type checked (size, location, equipment characteristics) Y N U 3. Gap at threaded anchor less than 1/4 inch Y N U N/A 4. Base stiffness and no significant prying action requirements met Y N U 5. Equipment base strength and structural load path adequate Y N U 6. Embedment steel and pads requirements met Y N U N/A 7. Embedment length requirements met Y N U 8. Anchor spacing requirements met Y N U 9. Edge distance requirements met Y N U 10. Concrete strength requirements met Y N U |  |

SEWS 8.1.3 (3 of 4)	Sheet 3 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) (Cont.) |  |  |
| --- | --- | --- |
| Equipment ID No.: | Equipment Class: Low-Voltage Switchgear |  |
| Equipment description: |  |  |
| Anchorage (Cont.) |  |  |
| 11. Concrete crack requirements met Y N U 12. Equipment with essential relays requirements met Y N U N/A 13. Installation adequacy requirements met Y N U N/A 14. No other concerns Y N U Does anchorage capacity exceed demand? Y N U Reference: |  |  |
| Interaction Effects (Chapter 7) |  |  |
| 1. Soft targets free from impact by nearby equipment or structures Y N U N/A 2. If equipment contains sensitive essential relays, equipment free from all impact by nearby equipment or structures Y N U N/A 3. Attached lines have adequate flexibility Y N U N/A 4. No collapse of overhead equipment, distribution systems, or masonry walls Y N N/A 5. Equipment is free from credible and significant seismic-induced flood and spray concerns Y N N/A 6. No credible seismic-induced fire concerns Y N N/A 7. No other “two over one” concerns as defined in DOE-STD-1021 Y N N/A 8. No other concerns Y N U N/A Is equipment free of interaction effects? Y N U |  |  |
| Comments |  |  |

SEWS 8.1.3 (4 of 4)	Sheet 4 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) (Cont.) |  |  |
| --- | --- | --- |
| Equipment ID No.: | Equipment Class: Low-Voltage Switchgear |  |
| Equipment description: |  |  |
| Comments (Cont.) |  |  |
| Screening Walkdown(s): Date Time Team Members |  |  |
| Recommend Resolution |  |  |
| q Maintenance action: q Further evaluation: q Retrofit design: q Other: q No further action required. Equipment is seismically adequate. |  |  |
| All aspects of the equipment's seismic adequacy have been addressed. Evaluation by: Date: (All team members) |  |  |