SEWS 8.1.5 (1 of 4)	Sheet 1 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) |  |  |
| --- | --- | --- |
| Equipment ID No.: | Equipment Class: Distribution Panels |  |
| Equipment description: |  |  |
| System: |  |  |
| Equipment Location: Bldg. | Floor El. | Room, Row/Col. |
| Manufacturer, model, etc.: |  |  |
| Weight of each Panel: |  |  |
| Wall mounted: | Floor mounted: |  |
| Drawing No.: | Performance Category: |  |
| Functionality Requirement |  |  |
| q Contact Lead Relay Reviewer to determine if item contains Essential Relays q For components whose function or structural integrity is required, complete all sections of this form. q For all other components, only anchorage evaluation is required. |  |  |
| Seismic Capacity vs. Demand (Chapter 5) |  |  |
| 1. Seismic Capacity based on: q Reference Spectrum q GERS q Existing documentation 2. Elevation where equipment receives seismic input Seismic Demand Spectrum (SDS) based on: q In-structure response spectrum (IRS) per DOE-STD-1020 q Other in-structure response spectrum (determine appropriate experience data scale factor) q Design basis earthquake (DBE) per DOE-STD-1020 q Other Scale Factor (SF) Experience Data Factor (FED) Does capacity exceed demand? Y N U Reference: |  |  |
| Caveats (Section 8.1.5) |  |  |
| Reference Spectrum (Identify with an asterisk (*) those caveats which are met by intent without meeting the specific wording of the caveat rule and explain the reason for this conclusion in the COMMENTS section below) |  |  |
| 1. Equipment is included in earthquake experience equipment class Y N U N/A 2. Contains only circuit breakers and switches Y N U N/A 3. All latches and fasteners in door secured Y N U N/A 4. Adjacent cabinets which are close enough to impact, or sections of multi-bay cabinets, are bolted together if they contain essential relays Y N U N/A 5. Wall- or floor-mounted NEMA type-enclosure Y N U N/A |  |  |

SEWS 8.1.5 (2 of 4)	Sheet 2 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) (Cont.) |  |
| --- | --- |
| Equipment ID No.: | Equipment Class: Distribution Panels |
| Equipment description: |  |
| Caveats (Cont.) |  |
| 6. Have you looked for and found no other adverse concerns? Y N U N/A Is the intent of all the caveats met for Reference Spectrum? Y N U N/A |  |
| GERS (Identify with an asterisk (*) those caveats which are met by intent without meeting the specific wording of the caveat rule and explain the reason for this conclusion in the COMMENTS section below) |  |
| 1. Equipment is included in generic seismic testing equipment class Y N U N/A 2. Meets all Reference Spectrum caveats Y N U N/A 3. If Switchboard GERS used, item is freestanding and designated as a switchboard by the manufacturer Y N U N/A 4. No Westinghouse Quicklag Type E Breakers Y N U N/A 5. Adjacent cabinets which are close enough to impact are bolted together Y N U N/A Is the intent of all the caveats met for GERS? Y N U N/A |  |
| Anchorage (Chapter 6) |  |
| 1. Type of anchorage: q expansion anchor q cast-in-place bolt or headed stud anchor q cast-in-place J-bolt q grouted-in-place bolt q welds to embedded steel on exposed steel q lead cinch anchors q Other q N/A (no further anchorage considerations) 2. Appropriate characteristics for anchorage type checked (size, location, equipment characteristics) Y N U 3. Gap at threaded anchor less than 1/4 inch Y N U N/A 4. Base stiffness and no significant prying action requirements met Y N U 5. Equipment base strength and structural load path adequate Y N U 6. Embedment steel and pads requirements met Y N U N/A 7. Embedment length requirements met Y N U 8. Anchor spacing requirements met Y N U 9. Edge distance requirements met Y N U 10. Concrete strength requirements met Y N U |  |

SEWS 8.1.5 (3 of 4)	Sheet 3 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) (Cont.) |  |
| --- | --- |
| Equipment ID No.: | Equipment Class: Distribution Panels |
| Equipment description: |  |
| Anchorage (Cont.) |  |
| 11. Concrete crack requirements met Y N U 12. Equipment with essential relays requirements met Y N U N/A 13. Installation adequacy requirements met Y N U N/A 14. No other concerns Y N U Does anchorage capacity exceed demand? Y N U Reference: |  |
| Interaction Effects (Chapter 7) |  |
| 1. Soft targets free from impact by nearby equipment or structures Y N U N/A 2. If equipment contains sensitive essential relays, equipment free from all impact by nearby equipment or structures Y N U N/A 3. Distribution lines have adequate flexibility Y N U N/A 4. No collapse of overhead equipment, distribution systems, or masonry walls Y N N/A 5. Equipment is free from credible and significant seismic-induced flood and spray concerns Y N N/A 6. No credible seismic-induced fire concerns Y N N/A 7. No other “two over one” concerns as defined in DOE-STD-1021 Y N N/A 8. No other concerns Y N U N/A Is equipment free of interaction effects? Y N U |  |
| Comments |  |

SEWS 8.1.5 (4 of 4)	Sheet 4 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) (Cont.) |  |
| --- | --- |
| Equipment ID No.: | Equipment Class: Distribution Panels |
| Equipment description: |  |
| Comments (Cont.) |  |
| Screening Walkdown(s): Date Time Team Members |  |
| Recommend Resolution |  |
| q Maintenance action: q Further evaluation: q Retrofit design: q Other: q No further action required. Equipment is seismically adequate. |  |
| All aspects of the equipment's seismic adequacy have been addressed. Evaluation by: Date: (All team members) |  |