SEWS 8.2.2 SOV (1 of 4)	Sheet 1 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) |  |  |
| --- | --- | --- |
| Equipment ID No.: | Equipment Class: Solenoid-Operated Valves |  |
| Equipment description: |  |  |
| Equipment Location: Bldg. | Floor El. | Room, Row/Col. |
| Manufacturer, model, etc.: |  |  |
| Smallest pipe diameter attached to valve: |  |  |
| Pipe centerline to top of motor actuator length: |  |  |
| Valve material: | Yoke material: |  |
| Weight: |  |  |
| Drawing No.: | Performance Category: |  |
| Functionality Requirement |  |  |
| q Contact Lead Relay Reviewer to determine if item contains Essential Relays q For components whose function or structural integrity is required, complete all sections of this form. q For all other components, only anchorage evaluation is required. |  |  |
| Seismic Capacity vs. Demand (Chapter 5) |  |  |
| 1. Seismic Capacity based on: q Reference Spectrum q GERS q Existing documentation 2. Elevation where equipment receives seismic input Seismic Demand Spectrum (SDS) based on: q In-structure response spectrum (IRS) per DOE-STD-1020 q Other in-structure response spectrum (determine appropriate experience data scale factor) q Design basis earthquake (DBE) per DOE-STD-1020 q Other Scale Factor (SF) Experience Data Factor (FED) Does capacity exceed demand? Y N U Reference: |  |  |
| Caveats (Section 8.2.2) |  |  |
| Reference Spectrum (Identify with an asterisk (*) those caveats which are met by intent without meeting the specific wording of the caveat rule and explain the reason for this conclusion in the COMMENTS section below) |  |  |
| 1. Equipment is included in earthquake experience equipment class Y N U N/A 2. No cast-iron body Y N U N/A 3. No cast-iron yoke Y N U N/A |  |  |

SEWS 8.2.2 SOV (2 of 4)	Sheet 2 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) (Cont.) |  |
| --- | --- |
| Equipment ID No.: | Equipment Class: Solenoid-Operated Valves |
| Equipment description: |  |
| Caveats (Cont.) |  |
| 4. Centerline of pipe to operator within restrictions or yoke can take static 3g load Y N U N/A 5. Actuator and yoke not braced independently from pipe Y N U N/A 6. Have you looked for and found no other adverse concerns? Y N U N/A Is the intent of all the caveats met for Reference Spectrum? Y N U N/A |  |
| GERS (Identify with an asterisk (*) those caveats which are met by intent without meeting the specific wording of the caveat rule and explain the reason for this conclusion in the COMMENTS section below) (Note that GERS for this class apply to only motor operator and its connection to valve; valve itself and valve/pipe interface are not covered.) |  |
| 1. Equipment is included in generic seismic testing equipment class Y N U N/A 2. Meets all Reference Spectrum caveats Y N U N/A 3. Use amplified spectrum for piping system at piping/valve interface Y N U N/A 4. Valve and operator will not impact surrounding structures and components Y N U N/A 5. Nominal pipe size is 1 inch or less Y N U N/A 6. Valve body is forged brass or steel Y N U N/A 7. Housing oriented in accordance with manufacturer's recommendations Y N U N/A 8. Height of valve (pipe centerline to top of housing) does not exceed 12 in. Y N U N/A 9. If SOV is a pilot on a larger valve, use amplified response spectrum at attachment point of SOV to larger valve Y N U N/A 10. Use 3.5g ZPA GERS for ASCO Type 206-381 Y N U N/A Is the intent of all the caveats met for GERS? Y N U N/A |  |
| Anchorage (Chapter 6) |  |
| 1. Type of anchorage: q expansion anchor q cast-in-place bolt or headed stud anchor q cast-in-place J-bolt q grouted-in-place bolt q welds to embedded steel on exposed steel q lead cinch anchors q Other q N/A (no further anchorage considerations) 2. Appropriate characteristics for anchorage type checked (size, location, equipment characteristics) Y N U 3. Gap at threaded anchor less than 1/4 inch Y N U N/A 4. Base stiffness and no significant prying action requirements met Y N U 5. Equipment base strength and structural load path adequate Y N U 6. Embedment steel and pads requirements met Y N U N/A |  |

SEWS 8.2.2 SOV (3 of 4)	Sheet 3 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) (Cont.) |  |
| --- | --- |
| Equipment ID No.: | Equipment Class: Solenoid-Operated Valves |
| Equipment description: |  |
| Anchorage (Cont.) |  |
| 7. Embedment length requirements met Y N U 8. Anchor spacing requirements met Y N U 9. Edge distance requirements met Y N U 10. Concrete strength requirements met Y N U 11. Concrete crack requirements met Y N U 12. Equipment with essential relays requirements met Y N U N/A 13. Installation adequacy requirements met Y N U N/A 14. No other concerns Y N U Does anchorage capacity exceed demand? Y N U Reference: |  |
| Interaction Effects (Chapter 7) |  |
| 1. Soft targets free from impact by nearby equipment or structures Y N U N/A 2. If equipment contains sensitive essential relays, equipment free from all impact by nearby equipment or structures Y N U N/A 3. Attached lines have adequate flexibility Y N U N/A 4. No collapse of overhead equipment, distribution systems, or masonry walls Y N N/A 5. Equipment is free from credible and significant seismic-induced flood and spray concerns Y N U N/A 6. No credible seismic-induced fire concerns Y N N/A 7. No other “two over one” concerns as defined in DOE-STD-1021 Y N N/A 8. No other concerns Y N U N/A Is equipment free of interaction effects? Y N U |  |
| Comments |  |

SEWS 8.2.2 SOV (4 of 4)	Sheet 4 of ______

| SCREENING EVALUATION WORK SHEET (SEWS) (Cont.) |  |  |
| --- | --- | --- |
| Equipment ID No.: | Equipment Class: Solenoid-Operated Valves |  |
| Equipment description: |  |  |
| Comments (Cont.) |  |  |
| Recommend Resolution |  |  |
| q Maintenance action: q Further evaluation: q Retrofit design: q Other: q No further action required. Equipment is seismically adequate. |  |  |
| All aspects of the equipment's seismic adequacy have been addressed. Evaluation by: Date: (All team members) |  |  |